|  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Note:   * Orders to operate must be performed in the number sequence listed * A group of operations listed under one sequence number may be performed by any sequence * Apparatus must be in the position stated in “OPERATION” column | | | | | | | |
| Purpose of Order:  **To isolate 54T1 at BU54SS under PC14 #000537** | | | | | | | |
| **Sequence Number** | **Device** | | **Remove tag no.** | **Operation** | **Place tag no.** | | **initials** |
|  | 54T1A Breaker | |  | Check Opened |  | |  |
|  | 54T1A-T1 | |  | Open and lock |  | |  |
|  | 54T1L4 Breaker | |  | Check Opened |  | |  |
|  | 54T1L4-T1 | |  | Open and lock |  | |  |
|  | 54T1-T1 | |  | Open and lock |  | |  |
|  | 54T1-G1 | |  | Close and lock |  | |  |
|  |  | |  |  |  | |  |
|  |  | |  |  |  | |  |
|  |  | |  |  |  | |  |
|  |  | |  |  |  | |  |
|  |  | |  |  |  | |  |
|  |  | |  |  |  | |  |
|  |  | |  |  |  | |  |
|  |  | |  |  |  | |  |
|  |  | |  |  |  | |  |
|  |  | |  |  |  | |  |
|  |  | |  |  |  | |  |
|  |  | |  |  |  | |  |
|  |  | |  |  |  | |  |
|  |  | |  |  |  | |  |
|  |  | |  |  |  | |  |
|  |  | |  |  |  | |  |
|  |  | |  |  |  | |  |
| Prepared By: | | Checked By: | | Ordered By: | | Completed By: | |
| Time: | | Time: | | Time: | | Time: | |
| Date: | | Date: | | Date: | | Date: | |
| Pinboard or Mimic board changed by: | | | | | | | |
|  | | | | PC 2 Serial Number: | | | |

 Serial No.: ……………………….. Date: ……………………………….. ORDER TO OPERATE (PC 17) Sheet …………… of ……….......